## Hot Work Checklist
Hot Work Permit and SWMS Control Checklist
A ready-to-use checklist that gates hot work through classification and permit, area clearance and combustible control, equipment, atmosphere and fume control, and a timed fire watch and cooldown sign-off.
Site / Facility: |  | Permit Number: |  | Work Order / Job No.: |  |  | Date:
Hot Work Type: |  | Permit Issuer (Competent Person): |  | Operator(s): |  |  | Fire Watch:
# | Control Gate | Control Requirement | Reference | Status | Evidence / Record | Responsible | Date Verified | Action Required | Closed
1 | 1. Classification and Permit | Work classified against the high risk construction work categories: an area that may hold a contaminated or flammable atmosphere, work in or near a confined space, and work on or near chemical, fuel, refrigerant or pressurised gas lines. | WHS Reg 291 | Yes | Hot work classification sheet HW-08 completed | J. Smith | 10/08/2026
2 | 1. Classification and Permit | SWMS prepared before the hot work starts, covering this location, this plant and these materials rather than a generic welding task. | WHS Reg 299 | Yes | SWMS HW-PLANT-03 briefed to the crew | J. Smith | 10/08/2026
3 | 1. Classification and Permit | Alternatives to hot work considered and recorded, for example mechanical cutting, bolted or clamped connections, or off-site prefabrication. | WHS Reg 36 | Yes | Core drilling trialled, penetration too large | J. Smith | 10/08/2026
4 | 1. Classification and Permit | Hot work permit issued in writing by a competent, authorised person who inspected the area first, and issued before any equipment is lit. | AS 1674.1 | Yes | Permit HW-2261 issued 07:40, area walked first | J. Smith | 10/08/2026
5 | 1. Classification and Permit | Permit names the specific location, the equipment, the authorised operators, the fire watch, the controls and the period it runs. | AS 1674.1
6 | 1. Classification and Permit | Total fire ban, site fire restriction, wind and weather conditions checked for the permit period and re-checked if conditions change. | WHS Reg 35
7 | 1. Classification and Permit | Re-validation rule stated on the permit: re-issue on shift change, on restart after a stoppage, on a change of conditions, or when the work moves outside the permitted area. | AS 1674.1
8 | 2. Area Preparation and Combustibles | Combustibles removed or protected within 15 metres of the hot work, both inside and outside the immediate work area. | AS 1674.1
9 | 2. Area Preparation and Combustibles | Area directly below the work inspected and cleared, including lower floors, voids, ceiling spaces, scaffold decks and stored product. | AS 1674.1 | Action Required | Cardboard pallet stack sits under the cut line | C. Brown | 10/08/2026 | Relocate the pallet stack and blanket the cable tray before the torch is lit. | No
10 | 2. Area Preparation and Combustibles | Area behind and beside the work inspected, including wall cavities, insulation, cladding, conveyor lines and adjacent plant. | AS 1674.1
11 | 2. Area Preparation and Combustibles | Floor and wall penetrations, expansion joints, service risers, drains and pits sealed or covered against falling sparks and slag. | AS 1674.1
12 | 2. Area Preparation and Combustibles | Fire resistant blankets, screens and shields in place to contain sparks and to protect bystanders and adjacent equipment. | AS 1674.1
13 | 2. Area Preparation and Combustibles | Flammable and combustible liquids, gases, dusts and fibres removed from the area, or isolated where removal is not reasonably practicable. | WHS Reg 355
14 | 2. Area Preparation and Combustibles | Suitable and accessible firefighting equipment provided at the work area, matched to the fire risk and confirmed in test date. | WHS Reg 359
15 | 2. Area Preparation and Combustibles | Work area isolated with signage and barriers, with safe entry and exit maintained and other workers informed of the hazards. | Construction Work CoP
16 | 3. Equipment, Atmosphere and Fume | Previous contents of any drum, tank, pipe or vessel identified and the safety data sheet reviewed before hot work starts. | Welding Processes CoP
17 | 3. Equipment, Atmosphere and Fume | Vessel prepared before hot work: caps and bungs removed, drained, and cleaned by the method the previous contents demand, with each compartment treated separately. | AS 1674.1
18 | 3. Equipment, Atmosphere and Fume | Atmosphere tested with a calibrated detector and flammable gas or vapour confirmed below 5 per cent of the lower explosive limit. Work stops and further controls apply above that level. | AS 1674.1
19 | 3. Equipment, Atmosphere and Fume | Residual atmosphere displaced with water or an inert gas where flammable residue may remain in seams and crevices. Pure oxygen is never used to purge or to blow down. | AS 1674.1
20 | 3. Equipment, Atmosphere and Fume | Flashback arrestors fitted on the operator side of each regulator connection and at the blowpipe. | AS 1674.1
21 | 3. Equipment, Atmosphere and Fume | Cylinders secured upright with valves protected, and hoses, regulators, leads and return connections inspected for cuts, abrasion, leaks and damage before the shift. | Welding Processes CoP
22 | 3. Equipment, Atmosphere and Fume | Ventilation provided and fume extraction placed as close as practicable to the point of welding, with exposure kept below the workplace exposure standard for welding fume. | WHS Reg 49
23 | 4. Fire Watch and Cooldown | Fire watch assigned with no other duties, correct firefighting equipment to hand, and the authority to stop the work. | AS 1674.1
24 | 4. Fire Watch and Cooldown | Fire watch positioned to see every area a spark can reach, including the level below and the far side of any wall, partition or floor penetration. | AS 1674.1
25 | 4. Fire Watch and Cooldown | Post-work cooldown watch period set by the risk assessment, with 30 minutes as the minimum and a longer period where insulation, voids, dust, timber or stored product are present. | AS 1674.1
26 | 4. Fire Watch and Cooldown | Cooldown watch maintained for the full period, with the finish time recorded against a named person rather than assumed. | AS 1674.1
27 | 4. Fire Watch and Cooldown | Final inspection carried out to confirm that no smouldering material remains in, under, behind or above the work area. | AS 1674.1
28 | 4. Fire Watch and Cooldown | Permit closed out and returned to the issuer, with the SWMS, the permit and the fire watch record retained on the project file. | WHS Reg 302
Hot Work Control Summary
Controls Verified (Yes): |  |  | 4 |  | Not Compliant (No): |  |  | 0
Action Required: |  |  | 1 |  | Not Yet Assessed: |  |  | 23
Hot Work Readiness: |  |  | INCOMPLETE - Assess every control before the permit is issued.
Fire Watch and Cooldown Sign-Off
Hot work ceased (time): |  |  |  | Cooldown period required (minutes):
Cooldown watch ended (time): |  |  |  | Final inspection clear (no smouldering):
Cooldown Status: |  |  | INCOMPLETE - Record the cooldown times and the final inspection result before the permit is closed.
Permit Issuer Sign-Off (Competent Person)
Name: |  |  |  | Signature: |  |  |  | Date / Time:
Copyright © MiSAFE Solutions Pty Ltd.

## Where Hot Work SWMS Fail
Where Hot Work SWMS Predictably Fail
# | Failure Pattern | Why It Fails | The Fix | Reference
1 | The work was never classified | Crews treat hot work as routine trade work, so nobody checks whether the area may hold a flammable or contaminated atmosphere and no SWMS is prepared. | Run every hot work job against the high risk construction work categories, including flammable atmosphere, confined space and fuel or gas lines, before the task rows are written. | WHS Reg 291, 299
2 | The permit is signed after the work | A permit completed at knock-off records history. It never gates anything, and the area inspection that should sit behind it never happens. | Issue the permit in writing before any equipment is lit, after a competent person has physically inspected the area. | AS 1674.1
3 | Only the immediate area is cleared | Sparks and slag travel and drop. The stack of packaging on the level below sits outside the welder line of sight and outside the cleared zone. | Clear or protect combustibles out to 15 metres, and physically walk the area below, behind and beside the work before the permit is issued. | AS 1674.1
4 | Penetrations left open | Floor openings, service risers, drains and wall gaps funnel molten metal straight into voids where nothing is watching. | Seal or cover every penetration, joint and drain in the spark path, and check them again after the first cut. | AS 1674.1
5 | Vessel contents assumed | Cutting into a drum or tank without identifying the previous contents ignites residue and vapour that no visual check would reveal. | Identify the previous contents, read the safety data sheet, then remove, drain, clean, test below 5 per cent of the LEL and displace the remaining atmosphere. | AS 1674.1
6 | Oxygen used to freshen or blow down | Oxygen enrichment feels harmless and makes clothing, oil and dust ignite violently from a small spark. | Purge with an inert gas only. Never use oxygen to ventilate a space or to blow dust off clothing, benches or plant. | AS 1674.1
7 | Fire watch has other duties | A fire watch who is also handing up tools or filling in paperwork is not watching. The smouldering starts in the seconds nobody is looking. | Assign a fire watch with no other duties, the right extinguishing equipment and the authority to stop the work. | AS 1674.1
8 | Watch stops when the torch stops | Most hot work fires start after the work finishes, once the crew has left and the smouldering material finds air. | Run a cooldown watch for the period the risk assessment sets, with 30 minutes as the minimum and longer where insulation, voids or stored product are present. | AS 1674.1
9 | No equipment inspection | A cut hose, a missing flashback arrestor or an unsecured cylinder turns a controlled flame into an uncontrolled one. | Inspect hoses, regulators, leads and connections before every shift, fit flashback arrestors at the regulator and blowpipe, and secure cylinders upright. | Welding Processes CoP
10 | Fume treated as a comfort issue | Welding fume carries a workplace exposure standard and individual components such as manganese and hexavalent chromium have their own limits. | Ventilate the area, place extraction as close as practicable to the arc, and assess exposure against the current welding fume standard. | WHS Reg 49
Copyright © MiSAFE Solutions Pty Ltd.

## Disclaimer & Copyright
Disclaimer
This template is a general guide only. It does not constitute legal advice and does not replace the requirement for advice tailored to your specific workplace, plant, materials, personnel, jurisdiction or activity. The user is responsible for ensuring compliance with all applicable Work Health and Safety legislation, regulations, codes of practice and Australian standards. MiSAFE Solutions Pty Ltd accepts no liability for any loss, damage, injury or legal action arising from use of, or reliance on, this template. For tailored advice, contact MiSAFE Solutions at misafesolutions.com.au.
Copyright
© 2026 MiSAFE Solutions Pty Ltd. All rights reserved. This template is provided as a free resource by MiSAFE Solutions and may be downloaded, copied and adapted by end users for internal compliance use within their own organisation. Redistribution, resale, or commercial reproduction in any form is prohibited without prior written consent from MiSAFE Solutions.
Copyright © MiSAFE Solutions Pty Ltd.