## Isolation Checklist
Electrical Isolation and Test Before Touch Checklist
A staged checklist that proves electrical isolation, from the identified isolation point to the tested tester and the re-energisation gate that stays shut until the work is finished.
Workplace / Site |  | Electrical Contractor / Licence No. |  | Isolation Point (board and circuit) |  | Work Type
12 Example Street, Anytown |  | Example Electrical Pty Ltd / EC012345 |  | DB-L3, Main isolator, Circuits 4 to 9 |  | De-energised switchboard alteration
Test Instrument (make / model / serial) |  | Known Live Source / Proving Unit |  | Safety Observer (energised work only) |  | Planned Date
Two-pole tester / MT-200 / SN 44821 |  | Proving unit PU-12 at DB-L3 |  | Not required, de-energised work |  | 14/09/2026
# | Stage | Checklist item | Status | Evidence / reference | Verified by | Date | Notes
1 | Before isolation | Scope of work confirmed and the electrical work SWMS prepared, signed by the crew and available on site (WHS Regs 291(k) and 299) | Yes | SWMS-026 current version | J. Smith | 14/09/2026
2 | Before isolation | Work planned as de-energised by default; any request to work energised tested against the four gates in WHS Reg 157 | Yes | Isolation plan, item 2 | J. Smith | 14/09/2026 | Tenant request declined
3 | Before isolation | Where energised work is unavoidable, a competent person has completed and recorded the risk assessment (WHS Reg 158) and it is retained for at least 28 days (WHS Reg 162) | N/A | No energised work planned | J. Smith | 14/09/2026
4 | Before isolation | Competent person nominated to carry out testing, and the test instrument recorded by make, model and serial number | Yes | Tester MT-200 SN 44821 | A. Jones | 14/09/2026
5 | Before isolation | Known live source or proving unit available at the work area | Yes | Proving unit PU-12 | A. Jones | 14/09/2026
6 | Isolation | Isolation point identified, recorded and under the control of the person carrying out the work | Yes | Photo IMG-4412 | A. Jones | 14/09/2026
7 | Isolation | Supply isolated at the identified point and the circuit chart marked up | Action Required | Circuit chart DB-L3 | A. Jones |  | Chart out of date, update before start
8 | Isolation | Isolating switch locked off, or conductors removed and tied back where locking is impractical
9 | Isolation | Personal padlock fitted by every worker exposed to the isolated conductors
10 | Isolation | Danger tag completed and signed by each lock owner; out-of-service tags used only for faulty equipment
11 | Isolation | Controls in place so the equipment cannot be inadvertently re-energised while work runs (WHS Reg 156)
12 | Prove dead | Tester proved on the known live source immediately before use
13 | Prove dead | Circuit tested at the work face by the competent person, with every exposed part treated as energised until proven otherwise (WHS Reg 155)
14 | Prove dead | Tester proved again on the known live source immediately after the test
15 | Prove dead | High voltage exposed parts earthed after de-energising (WHS Reg 155)
16 | Prove dead | Both ends of any cable checked for isolation before it is cut
17 | During work | Work area barricaded and signed so unauthorised persons are kept out (WHS Reg 159)
18 | During work | Adjacent live parts covered or insulated so nobody can inadvertently make contact (WHS Reg 160)
19 | During work | Safety observer present for energised work, competent to rescue and resuscitate and assessed within the last 12 months (WHS Reg 161)
20 | During work | Retest for dead completed on returning to the work area after any break
21 | During work | Site electrical equipment, leads and RCDs inspected, tested and recorded, and RCD protection provided where required (WHS Regs 150, 163 to 165, AS/NZS 3012)
22 | Re-energisation | Work complete, covers and barriers refitted, tools clear and no person exposed to the equipment
23 | Re-energisation | Each worker removed their own lock and tag; no lock removed by another person
24 | Re-energisation | Supply restored, tested and the result recorded with the time and the name of the person who restored it
Isolation Summary
Items verified (Yes): |  | 6 |  | Items failed (No): |  | 0
Action Required: |  | 1 |  | Not Applicable: |  | 0
INCOMPLETE - Work through every item before relying on this checklist. The isolation is not proven and the re-energisation gate stays shut.
Sign-Off
Role |  | Name |  | Signature |  | Date and time
Person carrying out the work (lock owner)
Safety observer (energised work only)
Supervisor / nominated responsible person
Copyright © MiSAFE Solutions Pty Ltd.

## Isolation Reference
Isolation, Live Work and Test Before Touch Reference
When energised electrical work is permitted (WHS Reg 157)
Gate | What it means | Example that passes | Evidence to keep
Health and safety | The work must be done energised in the interests of health and safety. | Life support or life-safety equipment that cannot be shut down. | Recorded risk assessment naming the safety reason.
Work cannot be done otherwise | The equipment must be energised for the work to be carried out properly. | Fault finding that only presents under load. | Recorded risk assessment and the safe work method statement.
Testing under Reg 155 | The work is the testing required to determine whether equipment is energised. | Proving a circuit dead before isolation is confirmed. | Test record with instrument, time and person.
No reasonable alternative | There is no reasonable alternative means of carrying out the work. | No isolation point exists and none can be created safely. | Documented options considered and rejected, with reasons.
Locks, tags and who removes them
Device | What it does | Who applies it | Who removes it
Personal danger lock | Physically prevents the isolating switch being operated while a person is exposed. | Every worker exposed to the isolated conductors, on the same hasp. | Only the worker who fitted it.
Danger tag | Names the person the isolation protects and warns others not to operate. | Each lock owner, signed and dated. | Only the signatory to the tag.
Out-of-service tag | Warns that equipment is faulty or unavailable for use. | The person who found or reported the fault. | The person who returns the equipment to service.
Group lock box | Holds the isolation key so a crew can each lock the box rather than the switch. | The person controlling the isolation, with each worker locking the box. | The last worker off the box, once every personal lock is removed.
Test before touch sequence (WHS Reg 155 and the model Code of Practice)
Step | Action | Why it matters | Record
1. Prove the tester | Test the instrument on a known live source or proving unit. | A dead tester reads every circuit as dead. | Instrument serial number and time.
2. Test the equipment | Test at the work face, treating every exposed part as energised until proven otherwise. | Isolation at the board does not prove the conductors at the work face. | Result, location and the competent person.
3. Prove the tester again | Return to the known live source and confirm the instrument still works. | Catches an instrument that failed between steps 1 and 2. | Second proving result and time.
4. Earth high voltage parts | Earth every high voltage exposed part after de-energising. | Stored and induced energy can re-energise a dead conductor. | Earths applied, by whom and when.
5. Retest on return | Repeat the sequence after any break or absence from the work area. | Someone may have restored supply while the area was unattended. | Retest entry against the checklist item.
Copyright © MiSAFE Solutions Pty Ltd.

## Disclaimer & Copyright
Disclaimer
This template is a general guide only. It does not constitute legal advice and does not replace the requirement for advice tailored to your specific workplace, plant, materials, personnel, jurisdiction or activity. The user is responsible for ensuring compliance with all applicable Work Health and Safety legislation, regulations, codes of practice and Australian standards. MiSAFE Solutions Pty Ltd accepts no liability for any loss, damage, injury or legal action arising from use of, or reliance on, this template. For tailored advice, contact MiSAFE Solutions at misafesolutions.com.au.
Copyright
© 2026 MiSAFE Solutions Pty Ltd. All rights reserved. This template is provided as a free resource by MiSAFE Solutions and may be downloaded, copied and adapted by end users for internal compliance use within their own organisation. Redistribution, resale, or commercial reproduction in any form is prohibited without prior written consent from MiSAFE Solutions.
Copyright © MiSAFE Solutions Pty Ltd.